## SUMMARY
MATERIAL TAKEOFF AND COST ESTIMATE STATEMENT
PROJECT NAME: |  | RENOVATION OF FAYETTE COUNTY JUSTICE CENTER
LOCATION: |  | 1 CENTER DRIVE, FAYETTEVILLE, GA 30214 |  | TOTAL AREA(SF) |  | 123858.8 | Area May Vary
Sr # | REFERENCE | DESCRIPTION |  |  | TOTAL COST | $COST/SF | 10.9488
DIVISION WISE SUMMARY | [6 empty] | 1084880.3721
CSI DIVISIONS
1 |  | 01-General Conditions |  |  | 0 | 0
2 |  | 02-Demolition Of Existing Items |  |  | 50518.75 | 0.40787
3 |  | 26-Electrical |  |  | 992736.5507 | 8.0151
4 |  | 28-Electronic Safety & security |  |  | 41625.0714 | 0.33607
SUB TOTAL | [6 empty] | 1084880.3721
OVERHEAD |  |  | 10% |  |  |  | 108488.0372
PROFIT |  |  | 10% |  |  |  | 108488.0372
INSURANCE |  |  | 0% |  |  |  | 0
CONTINGENCY |  |  | 5% |  |  |  | 54244.0186
NET TOTAL | [6 empty] | 1356100.4651
NOTES: PRICES OF LABOR AND MATERIALS ARE TAKEN FROM ONLINE MARKET RESOURCES AND CAN DIFFER FROM LOCAL VENDOR/SUPPLIER, RESPECTED CLIENTS ARE ADVISED TO DOUBLE CHECK TO MAKE SURE THE BID IS COMPETITIVE.

## ESTIMATE
Sr # | REFERENCE | DESCRIPTION | QUANTITY | WASTE | TOTAL QTY | UNIT | COST/UNIT | MATERIAL TOTAL | LABOR $/UNIT | TOTAL MANHOURS | EFFICIENCY (UNIT/HRs) | LABOR RATE | TOTAL LABOR COST | LABOR + MAT TOTAL COST | L+M UNIT COST
Units Legends; LS=Lump sum, LF=Linear Footage, CY=Cubic Yard, SF=Square Footage, EA=Count/Each
| PROJECT | RENOVATION OF FAYETTE COUNTY JUSTICE CENTER | [8 empty] | BUILDER COST |  | 1084880.3721
| ADDRESS | 1 CENTER DRIVE, FAYETTEVILLE, GA 30214 | [8 empty] | TOTAL BID COST |  | 1356100.4651
| 01. GENERAL CONDITIONS | [12 empty] | 0
INDIRECT PROJECT COSTS
1 |  | General Liability Insurance | 1 | 0% | 1 | LS | 0 | 0 | 0
2 |  | General Conditions (Backoffice Overhead) | 1 | 0% | 1 | LS | 0 | 0 | 0
DIRECT PROJECT COSTS
3 |  | Bonding Fee (If required) | 1 | 0% | 1 | LS | 0 | 0 | 0
4 |  | Permits | 1 | 0% | 1 | LS | 0 | 0 | 0
5 |  | Equipment Rental | 1 | 0% | 1 | LS | 0 | 0 | 0
6 |  | Travel, Tools, Gas | 1 | 0% | 1 | LS | 0 | 0 | 0
7 |  | Mobilization | 1 | 0% | 1 | LS | 0 | 0 | 0
8 |  | Temp. Facilities | 1 | 0% | 1 | LS | 0 | 0 | 0
9 |  | Temp. Signage and Protection | 1 | 0% | 1 | LS | 0 | 0 | 0
10 |  | Temp. Fencing | 1 | 0% | 1 | LS | 0 | 0 | 0
11 |  | Field Superintendent/Foreman (Full Time) | 1 | 0% | 1 | LS | 0 | 0 | 0
12 |  | Final Cleaning | 1 | 0% | 1 | LS | 0 | 0 | 0
| 02. DEMOLITION OF EXISTING ITEMS | [10 empty] | 55 |  | 50518.75
| E1.03-E1.41, E6.01 | DEMOLITION
13 |  | Disconnect Power From HVAC Equipment | 13 | 0% | 13 | EA | 0 | 0 | 82.59 | 19.5213 | 0.66594 | 55 | 1073.67 | 1073.67 | 82.59
14 |  | Remove Existing Junction Box | 15 | 0% | 15 | EA | 0 | 0 | 40.55 | 11.0591 | 1.3564 | 55 | 608.25 | 608.25 | 40.55
15 |  | Remove Existing Light Fixture | 558 | 0% | 558 | EA | 0 | 0 | 67.57 | 685.5284 | 0.81397 | 55 | 37704.06 | 37704.06 | 67.57
16 |  | Remove Existing Receptacle | 229 | 0% | 229 | EA | 0 | 0 | 47.3 | 196.94 | 1.1628 | 55 | 10831.7 | 10831.7 | 47.3
17 |  | Remove Existing Splice Box W/ Associated Wires & Conduits | 1 | 0% | 1 | EA | 0 | 0 | 93.85 | 1.7064 | 0.58604 | 55 | 93.85 | 93.85 | 93.85
18 |  | Remove Isolated Ground Bars | 2 | 0% | 2 | EA | 0 | 0 | 103.61 | 3.7676 | 0.53084 | 55 | 207.22 | 207.22 | 103.61
| 26. ELECTRICAL | [10 empty] | 55 |  | 992736.5507
| E2.03-E2.41 | WIRES & CONDUITS
19 |  | #12 AWG THWN Cu | 175774 | 5% | 184562.7 | LF | 0.33 | 60905.691 | 1.13 | 3611.3567 | 48.6726 | 55 | 198624.62 | 259530.311 | 1.4062
20 |  | #10 AWG THWN Cu | 44411 | 5% | 46631.55 | LF | 0.36 | 16787.358 | 1.13 | 912.4442 | 48.6726 | 55 | 50184.43 | 66971.788 | 1.4362
21 |  | #8 AWG THWN Cu | 1926 | 5% | 2022.3 | LF | 0.64 | 1294.272 | 1.13 | 39.5705 | 48.6726 | 55 | 2176.38 | 3470.652 | 1.7162
22 |  | #6 AWG THWN Cu | 1811.64 | 5% | 1902.222 | LF | 0.99 | 1883.1998 | 1.13 | 37.221 | 48.6726 | 55 | 2047.1532 | 3930.353 | 2.0662
23 |  | #4 AWG THWN Cu | 2832.32 | 5% | 2973.936 | LF | 1.52 | 4520.3827 | 1.13 | 58.1913 | 48.6726 | 55 | 3200.5216 | 7720.9043 | 2.5962
24 |  | 1/2" EMT Conduit | 75852 | 5% | 79644.6 | LF | 0.53 | 42211.638 | 1.88 | 2592.7593 | 29.2553 | 55 | 142601.76 | 184813.398 | 2.3205
25 |  | 3/4" EMT Conduit | 516 | 5% | 541.8 | LF | 1.083 | 586.7694 | 2.26 | 21.2029 | 24.3363 | 55 | 1166.16 | 1752.9294 | 3.2354
26 |  | 1" EMT Conduit | 452.91 | 5% | 475.5555 | LF | 1.62 | 770.3999 | 2.63 | 21.6573 | 20.9125 | 55 | 1191.1533 | 1961.5532 | 4.1248
27 |  | 1-1/4" EMT Conduit | 708.08 | 5% | 743.484 | LF | 2.7 | 2007.4068 | 3.01 | 38.7513 | 18.2724 | 55 | 2131.3208 | 4138.7276 | 5.5667
| E2.12, E2.22. E2.32, E2.41, | RECEPTACLES & DISCONNECT SWITCHES
28 |  | Duplex Receptacle | 1032 | 0% | 1032 | EA | 20.33 | 20980.56 | 45.79 | 859.1869 | 1.2011 | 55 | 47255.28 | 68235.84 | 66.12
29 |  | Floor Outlet Duplex Poke-Thru Device, Legrand Wiremold #6AT Revolution Series | 17 | 0% | 17 | EA | 785 | 13345 | 176.81 | 54.6504 | 0.31107 | 55 | 3005.77 | 16350.77 | 961.81
30 |  | Floor Outlet Quadruplex In Legrand Connectrac Receptacle | 5 | 0% | 5 | EA | 1341.46 | 6707.3 | 302.14 | 27.4673 | 0.18203 | 55 | 1510.7 | 8218 | 1643.6
31 |  | Floor Outlet Quadruplex Poke-Thru Device, Legrand Wiremold #6AT Revolution Series | 4 | 0% | 4 | EA | 785 | 3140 | 176.81 | 12.8589 | 0.31107 | 55 | 707.24 | 3847.24 | 961.81
32 |  | Floor Outlet Quadruplex Poke-Thru Device, Legrand Wiremold #8AT Revolution Series | 1 | 0% | 1 | EA | 773 | 773 | 174.11 | 3.1656 | 0.31589 | 55 | 174.11 | 947.11 | 947.11
33 |  | GFI Duplex Receptacle | 56 | 0% | 56 | EA | 22.54 | 1262.24 | 66.82 | 68.0349 | 0.82311 | 55 | 3741.92 | 5004.16 | 89.36
34 |  | GFI Quadruplex Receptacle | 2 | 0% | 2 | EA | 37.92 | 75.84 | 74.33 | 2.7029 | 0.73994 | 55 | 148.66 | 224.5 | 112.25
35 |  | Outlet Duplex In Legrand Connectrac System | 1 | 0% | 1 | EA | 1341.46 | 1341.46 | 302.14 | 5.4935 | 0.18203 | 55 | 302.14 | 1643.6 | 1643.6
36 |  | Quadruplex Receptacle | 38 | 0% | 38 | EA | 32.8 | 1246.4 | 74.33 | 51.3553 | 0.73994 | 55 | 2824.54 | 4070.94 | 107.13
37 |  | WP Duplex Receptacle | 4 | 0% | 4 | EA | 27.12 | 108.48 | 48.8 | 3.5491 | 1.127 | 55 | 195.2 | 303.68 | 75.92
38 | E2.33, E2.41 | 30A/2P Fused Disconnect Switch | 52 | 0% | 52 | EA | 98.28 | 5110.56 | 111.12 | 105.0589 | 0.49496 | 55 | 5778.24 | 10888.8 | 209.4
39 |  | 30A/2P/3R Fused Disconnect Switch | 3 | 0% | 3 | EA | 98.28 | 294.84 | 111.12 | 6.0611 | 0.49496 | 55 | 333.36 | 628.2 | 209.4
40 |  | 30A/3P Non-Fused Disconnect Switch | 1 | 0% | 1 | EA | 113.02 | 113.02 | 127.63 | 2.3205 | 0.43093 | 55 | 127.63 | 240.65 | 240.65
41 |  | 400A/3P/3R Fused Disconnect Switch | 2 | 0% | 2 | EA | 1506.9333 | 3013.8667 | 679.45 | 24.7073 | 0.080948 | 55 | 1358.9 | 4372.7667 | 2186.3833
42 |  | 60A/2P Fused Disconnect Switch | 5 | 0% | 5 | EA | 196.56 | 982.8 | 177.19 | 16.1082 | 0.3104 | 55 | 885.95 | 1868.75 | 373.75
43 |  | 60A/3P Fused Disconnect Switch | 1 | 0% | 1 | EA | 226.04 | 226.04 | 204.21 | 3.7129 | 0.26933 | 55 | 204.21 | 430.25 | 430.25
LIGHTING CONTROLS
44 | E2.03, 2.32, 2.33, 2.41 | Vault Fire Suppression System Control | 1 | 0% | 1 | EA | 671.95 | 671.95 | 320.51 | 5.8275 | 0.1716 | 55 | 320.51 | 992.46 | 992.46
45 |  | Motor Rated Switch | 16 | 0% | 16 | EA | 44.6 | 713.6 | 86.34 | 25.1171 | 0.63702 | 55 | 1381.44 | 2095.04 | 130.94
46 | E2.11,E2.21,E2.31 | Ceiling Mounted Combination Infrared / Ultrasonic Occupancy Sensor And Relay | 178 | 0% | 178 | EA | 52.2 | 9291.6 | 90.85 | 294.0236 | 0.60539 | 55 | 16171.3 | 25462.9 | 143.05
47 |  | Digital Switch, Current, Nxsw-Th3-Nxbtc | 1 | 0% | 1 | EA | 169.95 | 169.95 | 107.59 | 1.9562 | 0.5112 | 55 | 107.59 | 277.54 | 277.54
48 |  | Dimmer Switch | 134 | 0% | 134 | EA | 32.09 | 4300.06 | 72.83 | 177.4404 | 0.75518 | 55 | 9759.22 | 14059.28 | 104.92
49 |  | Four Way Switch | 4 | 0% | 4 | EA | 42.5 | 170 | 83.04 | 6.0393 | 0.66233 | 55 | 332.16 | 502.16 | 125.54
50 |  | Keyed Switch | 8 | 0% | 8 | EA | 19.99 | 159.92 | 39.04 | 5.6785 | 1.4088 | 55 | 312.32 | 472.24 | 59.03
51 |  | Low Voltage Switch For Overriding Lighting Relay | 30 | 0% | 30 | EA | 53.95 | 1618.5 | 61.42 | 33.5018 | 0.89547 | 55 | 1842.6 | 3461.1 | 115.37
52 |  | Single Pole Switch | 13 | 0% | 13 | EA | 18.5 | 240.5 | 42.05 | 9.9391 | 1.308 | 55 | 546.65 | 787.15 | 60.55
53 |  | Three Way Dimmer Switch | 26 | 0% | 26 | EA | 64.59 | 1679.34 | 109.99 | 51.9953 | 0.50005 | 55 | 2859.74 | 4539.08 | 174.58
54 |  | Three Way Switch | 15 | 0% | 15 | EA | 32.5 | 487.5 | 73.58 | 20.0673 | 0.74749 | 55 | 1103.7 | 1591.2 | 106.08
55 |  | Three Way Switch | 2 | 0% | 2 | EA | 32.5 | 65 | 73.58 | 2.6756 | 0.74749 | 55 | 147.16 | 212.16 | 106.08
56 |  | Wall Mounted Switch Infrared Occupancy Sensor | 37 | 0% | 37 | EA | 69.12 | 2557.44 | 96.1 | 64.6491 | 0.57232 | 55 | 3555.7 | 6113.14 | 165.22
| E2.11,E2.21,E2.31 | LIGHTING FIXTURES
57 |  | A, 2 X 4' Led Troffer, Columbia Lcat Series, Led 5400 Lumens, 40 Watts, 3500K | 469 | 0% | 469 | EA | 130.99 | 61434.31 | 108.18 | 922.4804 | 0.50841 | 55 | 50736.42 | 112170.73 | 239.17
58 |  | A-EM, 2 X 4' Led Troffer W/ Emergency Battery Backup, Columbia Lcat Series, Led 5400 Lumens, 40 Watts, 3500K | 83 | 0% | 83 | EA | 165.99 | 13777.17 | 137.09 | 206.8813 | 0.4012 | 55 | 11378.47 | 25155.64 | 303.08
59 |  | D, 6" Round Downlight, Prescolite Lfr-6Rd, Led 3000 Lumens, 26 Watts, 3500K | 302 | 0% | 302 | EA | 24.95 | 7534.9 | 20.61 | 113.1676 | 2.6686 | 55 | 6224.22 | 13759.12 | 45.56
60 |  | D2, 6° Round Downlight, Prescolite Lfr-6Rd, Led 1500 Lumens, 12 Watts, 3500K | 81 | 0% | 81 | EA | 24.95 | 2020.95 | 20.61 | 30.3529 | 2.6686 | 55 | 1669.41 | 3690.36 | 45.56
61 |  | D2-EM, 6° Round Downlight W/ Emergency Battery Backup , Prescolite Lfr-6Rd, Led 1500 Lumens, 12 Watts, 3500K | 20 | 0% | 20 | EA | 59.95 | 1199 | 49.51 | 18.0036 | 1.1109 | 55 | 990.2 | 2189.2 | 109.46
62 |  | D2G, 6° Round Downlight, Prescolite Lfr-6Rd, Led 1500 Lumens, 12 Watts, 3500K | 29 | 0% | 29 | EA | 24.95 | 723.55 | 20.61 | 10.8671 | 2.6686 | 55 | 597.69 | 1321.24 | 45.56
63 |  | D2G-EM, 6° Round Downlight W/ Emergency Battery Backup, Prescolite Lfr-6Rd, Led 1500 Lumens, 12 Watts, 3500K | 5 | 0% | 5 | EA | 59.95 | 299.75 | 49.51 | 4.5009 | 1.1109 | 55 | 247.55 | 547.3 | 109.46
64 |  | D-EM, 6" Round Downlight W/ Emergency Battery Backup, Prescolite Lfr-6Rd, Led 3000 Lumens, 26 Watts, 3500K | 142 | 0% | 142 | EA | 59.95 | 8512.9 | 49.51 | 127.8258 | 1.1109 | 55 | 7030.42 | 15543.32 | 109.46
65 |  | DG, 6" Round Downlight, Prescolite Lfr-6Rd, Led 3000 Lumens, 26 Watts, 3500K | 33 | 0% | 33 | EA | 59.95 | 1978.35 | 49.51 | 29.706 | 1.1109 | 55 | 1633.83 | 3612.18 | 109.46
66 |  | DG-EM, 6" Round Downlight W/ Emergency Battery Backup, Prescolite Lfr-6Rd, Led 3000 Lumens, 26 Watts, 3500K | 9 | 0% | 9 | EA | 59.95 | 539.55 | 49.51 | 8.1016 | 1.1109 | 55 | 445.59 | 985.14 | 109.46
67 |  | Dw, 6° Round Wall Wash, Prescolite Lfr-6Rw, Led 1500 Lumens, 12 Watts, 3500K | 45 | 0% | 45 | EA | 24.95 | 1122.75 | 20.61 | 16.8627 | 2.6686 | 55 | 927.45 | 2050.2 | 45.56
68 |  | T, 1' X 4' Vandal Resistant Fixture, La Lighting Fse110, Led 3600 Lumens, 30 Watts, 3500K | 4 | 0% | 4 | EA | 307.65 | 1230.6 | 184.78 | 13.4385 | 0.29765 | 55 | 739.12 | 1969.72 | 492.43
69 |  | T-EM, 1' X 4' Vandal Resistant Fixture W/ Emergency Battery Backup, La Lighting Fse110, Led 3600 Lumens, 30 Watts, 3500K | 26 | 0% | 26 | EA | 342.65 | 8908.9 | 205.8 | 97.2873 | 0.26725 | 55 | 5350.8 | 14259.7 | 548.45
70 |  | U, 4' Utility Strip Light, Columbia Mps Series, Led 3800 Lumens, 27 Watts, 3500K | 8 | 0% | 8 | EA | 105.6 | 844.8 | 87.21 | 12.6851 | 0.63066 | 55 | 697.68 | 1542.48 | 192.81
71 |  | U-EM, 4' Utility Strip Light W/ Emergency Battery Backup, Columbia Mps Series, Led 3800 Lumens, 27 Watts, 3500K | 9 | 0% | 9 | EA | 140.6 | 1265.4 | 116.12 | 19.0015 | 0.47365 | 55 | 1045.08 | 2310.48 | 256.72
72 |  | X-1, Single Face Edge-Lit Exit Sign, Compass Cel, With Integral Battery, LED | 69 | 0% | 69 | EA | 135.7 | 9363.3 | 112.07 | 140.5969 | 0.49076 | 55 | 7732.83 | 17096.13 | 247.77
73 |  | X-2, Double Face Edge-Lit Exit Sign, Compass Cel, With Integral Battery, LED | 8 | 0% | 8 | EA | 135.7 | 1085.6 | 112.07 | 16.3011 | 0.49076 | 55 | 896.56 | 1982.16 | 247.77
74 |  | X-R, Single Face Vandal Resistant Exit Sign, Daul-Lite Dync With Integral Battery, LED | 4 | 0% | 4 | EA | 975.1 | 3900.4 | 366.04 | 26.6211 | 0.15026 | 55 | 1464.16 | 5364.56 | 1341.14
| E6.01 | POWER DISTRIBUTION
75 |  | 100A, 208/120V, 3PH 4W Panel LR3A | 1 | 0% | 1 | EA | 360 | 360 | 255.26 | 4.6411 | 0.21547 | 55 | 255.26 | 615.26 | 615.26
76 |  | 100A, 208/120V, 3PH 4W Panel LR3WA | 1 | 0% | 1 | EA | 360 | 360 | 255.26 | 4.6411 | 0.21547 | 55 | 255.26 | 615.26 | 615.26
77 |  | SPD, Surge Protection Device | 8 | 0% | 8 | EA | 89.98 | 719.84 | 83.04 | 12.0785 | 0.66233 | 55 | 664.32 | 1384.16 | 173.02
78 |  | Splice Box | 1 | 0% | 1 | EA | 32 | 32 | 39.57 | 0.71945 | 1.3899 | 55 | 39.57 | 71.57 | 71.57
| E8.04-E8.08 | CIRCUIT BREAKERS
79 |  | 100A/3P Breaker | 2 | 0% | 2 | EA | 178.55 | 357.1 | 161.42 | 5.8698 | 0.34073 | 55 | 322.84 | 679.94 | 339.97
80 |  | 175A/3P Breaker | 1 | 0% | 1 | EA | 312.4625 | 312.4625 | 211.72 | 3.8495 | 0.25978 | 55 | 211.72 | 524.1825 | 524.1825
81 |  | 200A/3P Breaker | 1 | 0% | 1 | EA | 357.1 | 357.1 | 241.75 | 4.3955 | 0.22751 | 55 | 241.75 | 598.85 | 598.85
82 |  | 20A/1P Breaker | 543 | 0% | 543 | EA | 25.67 | 13938.81 | 35.29 | 348.4085 | 1.5585 | 55 | 19162.47 | 33101.28 | 60.96
83 |  | 20A/1P GFCI Breaker | 7 | 0% | 7 | EA | 25.67 | 179.69 | 35.29 | 4.4915 | 1.5585 | 55 | 247.03 | 426.72 | 60.96
84 |  | 20A/3P Breaker | 5 | 0% | 5 | EA | 35.71 | 178.55 | 48.8 | 4.4364 | 1.127 | 55 | 244 | 422.55 | 84.51
85 |  | 25A/1P GFCI Breaker | 4 | 0% | 4 | EA | 32.0875 | 128.35 | 43.55 | 3.1673 | 1.2629 | 55 | 174.2 | 302.55 | 75.6375
86 |  | 30A/2P Breaker | 3 | 0% | 3 | EA | 48 | 144 | 65.32 | 3.5629 | 0.84201 | 55 | 195.96 | 339.96 | 113.32
87 |  | 30A/3P Breaker | 8 | 0% | 8 | EA | 53.565 | 428.52 | 72.83 | 10.5935 | 0.75518 | 55 | 582.64 | 1011.16 | 126.395
88 |  | 30A/3P GFCI Breaker | 1 | 0% | 1 | EA | 53.565 | 53.565 | 72.83 | 1.3242 | 0.75518 | 55 | 72.83 | 126.395 | 126.395
89 |  | 40A/1P Breaker | 5 | 0% | 5 | EA | 51.34 | 256.7 | 69.83 | 6.3482 | 0.78763 | 55 | 349.15 | 605.85 | 121.17
90 |  | 45A/3P Breaker | 2 | 0% | 2 | EA | 80.3475 | 160.695 | 108.87 | 3.9589 | 0.50519 | 55 | 217.74 | 378.435 | 189.2175
91 |  | 50A/3P Breaker | 1 | 0% | 1 | EA | 89.275 | 89.275 | 120.88 | 2.1978 | 0.455 | 55 | 120.88 | 210.155 | 210.155
92 |  | 600A/3P Breaker | 1 | 0% | 1 | EA | 1071.3 | 1071.3 | 482.75 | 8.7773 | 0.11393 | 55 | 482.75 | 1554.05 | 1554.05
93 |  | 60A/3P GFCI Breaker | 1 | 0% | 1 | EA | 107.13 | 107.13 | 120.88 | 2.1978 | 0.455 | 55 | 120.88 | 228.01 | 228.01
94 |  | 70A/3P Breaker | 2 | 0% | 2 | EA | 124.985 | 249.97 | 141.15 | 5.1327 | 0.38966 | 55 | 282.3 | 532.27 | 266.135
MISCELLANEOUS
95 | E2.03-E2.33 | Junction Box | 24 | 0% | 24 | EA | 17 | 408 | 38.29 | 16.7084 | 1.4364 | 55 | 918.96 | 1326.96 | 55.29
| 28. ELECTRONIC SAFETY & SECURITY | [10 empty] | 55 |  | 41625.0714
| FA-21 | WIRES & CONDUITS
96 |  | #14 FPL | 3751.92 | 5% | 3939.516 | LF | 0.16 | 630.3226 | 1.13 | 77.0849 | 48.6726 | 55 | 4239.6696 | 4869.9922 | 1.2362
97 |  | #16 FPL | 3434.44 | 5% | 3606.162 | LF | 0.13 | 468.8011 | 1.13 | 70.5621 | 48.6726 | 55 | 3880.9172 | 4349.7183 | 1.2062
98 |  | 1/2" EMT Conduit | 3594 | 5% | 3773.7 | LF | 0.53 | 2000.061 | 1.88 | 122.8495 | 29.2553 | 55 | 6756.72 | 8756.781 | 2.3205
FIRE ALARM DEVICES
99 |  | Fire Alarm Horn Strobe | 32 | 0% | 32 | EA | 72.49 | 2319.68 | 78.84 | 45.8705 | 0.69762 | 55 | 2522.88 | 4842.56 | 151.33
100 |  | Fire Alarm Pull Station | 17 | 0% | 17 | EA | 44.33 | 753.61 | 88.6 | 27.3855 | 0.62077 | 55 | 1506.2 | 2259.81 | 132.93
101 |  | Fire Alarm Strobe | 33 | 0% | 33 | EA | 54 | 1782 | 76.58 | 45.948 | 0.7182 | 55 | 2527.14 | 4309.14 | 130.58
102 |  | RFAP, Fire Response & Alarm Panel | 1 | 0% | 1 | EA | 1350 | 1350 | 506.77 | 9.214 | 0.10853 | 55 | 506.77 | 1856.77 | 1856.77
103 |  | Smoke Detector | 70 | 0% | 70 | EA | 52.19 | 3653.3 | 96.1 | 122.3091 | 0.57232 | 55 | 6727 | 10380.3 | 148.29
NOTES FOR CLIENTS | [9 empty] | SUBTOTAL |  |  |  |  | 1084880.3721
THIS EXCEL STATEMENT IS EDITABLE AND CAN BE MODIFIED AS NEEDED.
GENERAL CONDITIONS
[10 empty] | OVERHEAD |  |  | 10% |  | 108488.0372
[10 empty] | PROFIT |  |  | 10% |  | 108488.0372
[10 empty] | INSURANCE |  |  | 0% |  | 0
[10 empty] | CONTINGENCY |  |  | 5% |  | 54244.0186
1356100.4651
[10 empty] | 12990.4268 | Total Man-hours
[10 empty] | 10 | Crew Size
[10 empty] | 162.3803 | Working Days
[10 empty] | 8.119 | Months